{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":11,"n_cols":17,"rows_kept":11,"merged":[[0,0,0,14],[10,0,10,14]],"flags":["formulas_cached_only"]}
["水处理设备清单"]
["序号","编号","材料名称","型号","规格","单位","数量","单价","合计","品牌","不含税单价","不含税合价","含税单价（13%增值税）","含税合价（13%增值税）","备注"]
[1,"DY-1","真空排气定压机组","DY2/90+NT1000","适用水温：0-70℃，公称总容积：1000L,有效容积:1000L,补水泵启动压力P1：760kpa，补水泵停泵压力P2：911kpa，电磁阀开启压力P3：1012kpa，安全阀开启压力P4：1125kpa，补水泵流量：2m3/h.补水泵扬程：600kpa，电源：220v，功率：1.5*2kw，外形尺寸：1700*900*2600，重量：1500kg","台",1,26840,26840,"常州瑞源",{"$nulls":4},"1非承压式\n2一体式机组，罐体常压，有效容积达到全容积的95%，双泵配置定点控制精度±0.2bar，带有自动减压泄水功能",24000,24000]
[2,"FWT BF-2","全自动示踪加药装置系统","WD-1JY-GZC","最大加药量5L/h，P=220W，重量290kg；微电脑控制，自动运行，自带药剂桶、计量泵、液位控制器","套",1,14500,14500,"常州瑞源",{"$nulls":6},12250]
[3,"CCE B1-1","旁流式综合水处理器","WD-80PLZH/I-1.0","适配管径DN400，P=600W，重量350kg；微电脑控制，自动运行","套",1,12500,12500,"常州瑞源",{"$nulls":6},9500]
[4,"CWE-B1-1","水箱消毒机 ",null,"N=1.5KW，杀菌率＞99.5% 灭藻率>99.9% ","台",1,9250,9250,"常州瑞源",{"$nulls":5},9250,8325]
[5,"JY-1","化学加药装置",null,"处理流量：500m3/h，加药桶容量：200L，工作压力：1.0mpa，电源：220v，功率：0.2kw，外形尺寸：1320*1150*1600，重量：400kg.","台",1,12500,12500,"常州瑞源",{"$nulls":4},"双桶双泵，全自动控制可实现远程监控。可根据用户需求配置不同在线监测，仪表配有PH探头，电导率探头",12500,11250]
[6,"JQ-1，2","冷凝器清洗装置",null,"发球机：发球水量≥8L/S，扬程≥20MH20,发球时间＜3s；\n补球机：管径：250mm，局部阻力：5kpa，承压：1.0pa；\n电源：380v，功率：2.2kw","台",2,18420,36840,"常州瑞源",{"$nulls":4},"(法兰连接)DN250，自带集污装置集中污垢并排放",18420,16578]
[7,"PWQ-1","微泡排气除污装置",null,"管径：DN350,重量：2000kg，工作压力：1.6mpa","台",1,15460,15460,"常州瑞源",{"$nulls":4},"(法兰连接)DN350",10000,11500]
[8,"PWQ-2","微泡排气除污装置",null,"管径：DN250,重量：1000kg，工作压力：1.0mpa","台",1,11280,11280,"常州瑞源",{"$nulls":4},"(法兰连接)DN250",8000,8000]
["含运费、指导安装及调试"]